## TEST SUMMARY
General Test Information
Test Attempt | 1
Date Test Started - Date Test Finished | 17/04/2026 - ?????
System | BMS
System Owner | Sauter
Manufacturer | Sauter
Model | EY6AS80
Firmware Version | V3.3.1b5450
Serial Number | 711150000659
Name Of Tester | Dhilen Patel / Zakariya Amos
TEST RESULT | PASS
Test Summary
The device has passed the IP device qualification, no issues were found from the scans/tests.

## TESTPLAN
Test Results Explained PASS - The device passed the specific test with no issues. FAIL - The device failed the specific test. Where the reasons for the failure will be specified in the test comments. ADVISORY - The test is close to passing, but further configuration is required to get the device to be compliant. E.g. HTTP is open by default, which is unencrypted, but you are able to disable HTTP in the device's web interface. INFO - The test is for information only and may not cause the device to pass/fail. Note that depending on the test result, an INFO only test result can cause the device to fail. N/A - The test is not applicable to the device and therefore was not conducted.
Test Number | Brief Description | Test Description | Essential Test | Test Result | Test Comments
1 | Initial Switch Connection | When device is plugged in to a switch, it auto-negotiates a speed and supports full duplex. Confirm device supports manual speed and duplex. | YES | PASS | Speed auto-negotiates to 100Mbit/sec. Manual speeds of 10 and 100Mbit/sec supported.
2 | Static IP | Confirm that the device can have a static IPv4 address set. | YES | PASS
3 | DHCP #1 | Device accepts IP address and related data via DHCP. | YES | PASS
4 | DHCP #2 | Device accepts changed IP address from the DHCP server without the need of a reboot or port toggle. | YES | PASS | DHCP range changed, device was able to go onto the new range without a port toggle.
5 | DNS Support | Device supports DNS and static/dynamic DNS addressing. | YES | PASS | Static DNS supported only.
6 | Hostname Resolutions | Can M2M connections be made via hostname rather than IP, e.g. MQTT Broker connection? | YES (IoT GATEWAYS ONLY) | PASS | Device is not acting as an IoT gateway on this project, but server fields require an IP address to be filled in rather than a hostname. This is not an issue as DNS is supported and can be pointed at a local DNS if required.
7 | Ping | Device responds to ping requests. | YES | PASS
8 | MAC Address | Note the MAC address and confirm it is registered to a manufacturer. | YES | PASS | LAN MAC: 0C:1C:57:14:52:24 Vendor: Texas Instruments Company Address: 12500 TI Blvd Dallas TX US 75243 Last Updated: 12/04/2018 WAN MAC: 0C:1C:57:F4:52:22
9 | IPv6 #1 | Device supports IPv6 addressing. | INFO | INFO
10 | IPv6 #2 | Device supports SLAAC/DHCP for IPv6 addressing. | INFO | INFO | DHCP IPv6 address received by the device.
11 | Network Reconnection | Device automatically re-discovers network connection when network cable is toggled. | YES | PASS
12 | NTP | Device can automatically synchronise to NTP highest version supported (ideally version 4). Device allows for a static/dynamic NTP server addressing. | YES (IoT GATEWAYS ONLY)
13 | Data Flow | Record the devices data flow types. endpoints and keepalive traffic. There should be no unencrypted communications. | YES | PASS | No unusual traffic.
14 | Secondary Device Access | Check the device for secondary ports and/or any other means of creating a network connection to the device. | INFO | INFO | There is a WAN ethernet port, a USB port and SD card.
15 | Open Ports | List the network ports that are currently open on the device. | INFO | INFO | Network ports open on physical LAN ports G, H, J: PORT STATE SERVICE 80/tcp open http 443/tcp open https 5627/tcp open CASE Sun Config (WSC) 16080/tcp open 16443/tcp open 44443/tcp open license manager port 44444/tcp open license manager port Network ports open on physical WAN port: 443/tcp https
16 | Discouraged Ports | List the network ports that are currently open, but should be closed (e.g. due to being unencrypted or unused). | YES |  | HTTP is only being used to direct the user to HTTPS. Port 5627 is used by the CASE Sun Configuration tool to configure the Sauter device. CASE Sun discovery service is implemented on UDP port 5353. TCP ports 44443 and 44444 - license manager ports for updating the licenses on the controller - e.g. MQTT, API, BACnet Sec and etc.
17 | TLS Version | Where the device utilises TLS, list the lowest version of TLS supported. This should be TLSv1.2 or above. | YES | PASS | TLSv1.3 supported.
18 | Ciphersuites | List the ciphersuites supported by the device and highlight any that are deemed as weak by Mozilla standards. | INFO | INFO | TLS_AES_256_GCM_SHA384 TLS_CHACHA20_POLY1305_SHA256 TLS_AES_128_GCM_SHA256
19 | Unencrypted Web Access | The device does not accept unencrypted web traffic and supports x509 certificates. | YES | PASS | HTTPS supported, user is redirected to HTTPS if standard HTTP is used.
20 | x509 Certificate Updates | Device allows for replacement of self-signed certificate with an x509 certificate. | INFO | INFO | Device allows for replacement of certificate in the web GUI in TLS Settings.
21 | 802.1x | Device supports 802.1x and supports EAP-TLS. | INFO | INFO | 802.1x support can be enabled with an additional license. TBC 802.1x authentication methods accepted.
22 | BACnet/IP Support and BACnet/IP Version | Does the device support BACnet/IP? Record the BACnet version and traffic to and from the device. | INFO | INFO | BACnet/IP supported. PORT STATE SERVICE 47808/udp open bacnet ¦ bacnet-info: ¦ Vendor ID: Fr. Sauter AG (80) ¦ Vendor Name: SAUTER ¦ Object-identifier: 1 ¦ Firmware: V3.3.1b5450 ¦ Application Software: 3.7 ¦ Object Name: AS1 ¦ Model Name: EY6AS80F021 ¦ Description: ¦_ Location: MAC Address: 0C:1C:57:F4:52:24 (Texas Instruments)
23 | BACnet PIC/BIBB | Confirm the device has a valid BACnet PIC and BIBB statement. | INFO | INFO | Yes, both PIC and BIBB statement.
24 | SSH | Does the device require the use of SSH? If required, confirm SSH protocol version 2 is being used. | YES | N/A | SSH not supported.
25 | MQTT Support | Does the device support MQTT? If so state the MQTT versions supported. If not, state how the device can send data to a broker (e.g. via HTTPS or via middleware). | YES (IoT GATEWAYS ONLY) | N/A | Not acting as an IoT gateway on this project, so N/A
26 | MQTT Custom Payloads | Does the device support UDMI JSON payload creation? Does the device allow custom JSON payloads to be created? | YES (IoT GATEWAYS ONLY) | N/A
27 | MQTT Write-back | Does the device allow commands to be sent via MQTT? | YES (IoT GATEWAYS ONLY) | N/A
28 | MQTT Over TLS | Does the device support MQTT over TLS? | YES (IoT GATEWAYS ONLY) | N/A
29 | MQTT Authentication #1 | Is Client Certificate authentication for MQTT supported using X.509 certificates? | YES (IoT GATEWAYS ONLY) | N/A
30 | MQTT Authentication #2 | Is Username/Password authentication for MQTT supported? | YES (IoT GATEWAYS ONLY) | N/A
31 | PKI Integration | Can custom CA certificates be installed into the devices trust store to enable integration into a private PKI? | YES (IoT GATEWAYS ONLY) | N/A | CAs can be uploaded via the web GUI.
32 | Wi-Fi Standards Supported | The device supports one or more of the following Wi-Fi standards: 802.11g / 802.11n / 802.11ac / 802.11ax | YES | N/A | Wi-Fi not supported.
33 | Wi-Fi Disablement | If not required for normal operations: Wi-Fi can be disabled on the device. | YES | N/A
34 | Wi-Fi Encryption | Wi-Fi supports WPA2-AES as a minimum. | YES | N/A
35 | PoE | List the PoE standards supported by the device. | INFO | N/A | PoE not supported.
36 | Credentials | Confirm the default credentials on the device and confirm the credentials can be changed for each credential-based service. | YES | PASS | Credentials can be changed.
37 | Login Credentials Policy | Confirm the login credentials policy on all services that require username/password authentication. | INFO | INFO | Web server password policy: Value must have between 8 and 256 characters, including 1 lower-case, 1 upper-case and 1 non-alphanumerical character(s): /.-,+*)('&%$#"! @?>=<;:`_^]\[~}¦{ The required password complexity/policy can be altered in the web GUI, as well as the password duration and two factor authentication.
38 | Brute Force | Device employs brute force protection on all of it's credential-based services. | YES | PASS | After around 5 unsuccessfull login attempts, you get the following message: Your IP has been locked out.
39 | Session Expiry | Device logs out the user on inactivity after a certain period of time. | INFO | INFO | Authentication Duration can be set in the web GUI - the user is logged out of the webpage on inactivity.
40 | Firmware Upgrades | Confirm how the firmware of device can be upgraded. | INFO | INFO | The firmware can be upgraded using the Sauter Sun Configuration tool.
41 | Software/OS Info | List any software/OS version information obtained from the device. | INFO | INFO | nginx is used for the webserver, but the specific version could not be identified.
42 | Additional Information | Device is scanned for any further vulnerabilities, please refer to the "Additional Information" tab. | YES | PASS | Nothing unusual came up on the scans. However, it is recommended to add HSTS, X-Content-Type-Options, Content-Security-Policy and Referrer-Policy to make the HTTP headers more secure.
43 | SOAK | Leave the device connected to the network for seven days, check switch logs to ensure the port remained stable and the device can still be reached. | YES | PASS | Device remained connected to the test lab's network with no issues.