## Synopsis
System Owner - Device Testing - EasyIO FW-08
1st Test Attempt
Device Details
Manufacturer | EasyIO
Model | FW-08
Serial Number | 40411237
Firmware | V1.0b20
Test Details
Tester | Dhilen Patel
Test Start Date | 2023-05-02
Test End Date | 2023-05-16
Test Results
RESULT | FAIL
Test Synopsis
Q11 - Secondary port should be disabled. Q21 - Weak/old Ciphersuite should be disabled. Q36. A couple TCP ports are open that are not on the whitelist. Q44: Multiple identified risks in the Nessus scan, please see "01 Test - Nessus" for more information.

## Protocol Whitelist
Protocol Whitelist
This protocol whitelist determines the allowed services on network. The IANA assigned ports are listed against the services, however there may be instances where services are running on a non-assigned port. If a device uses a port outside of the whitelist, then it will be deemed non-compliant unless justified.
Item | Protocol | Connection | IANA Assigned Port
1 | Secure File Transfer Protocol (sFTP) (RFC 959) | TCP | 22
3 | Dynamic Host Configuration Protocol (DHCP) (RFC 2131) | UDP | 68
4 | Domain Name System (DNS) (RFC 1034) | TCP/UDP | 53
5 | Hypertext Transfer Protocol (HTTPs) (RFC 2616) | TCP | 443
6 | Network Time Protocol (NTP) (RFC 5905) | UDP | 123
7 | Simple Network Management Protocol (SNMPv3) (RFC 1901-1908, 3411-3418) | TCP/UDP | 161
8 | Lightweight Directory Access Protocol over TLS/SSL (LDAPS) (RFC 4513) | TCP/UDP | 636
9 | FTPS (FTP over TLS) (RFC 959, 2228, 4217) | TCP/UDP | 989/990
10 | MQTTS (MQTT over TLS) | TCP/UDP | 8883
11 | BACnet (Building Automation and Control Network) | TCP/UDP | 47808

## 01 Test - Questions
Purpose
This test aims to review a device against a list of functionality and security questions to identity its security level and what features/functions that it does/does not supports. It will have to pass all required "Essential Pass" questions to receive the outcome of a "PASS", if not it will receive a "FAIL" or "ADVISORY". A "PASS" result does not guarantee there are no security issues with the device, but only that it has met the requirements of this test plan at the point it was tested. Some questions will be informational based only, these questions will not be rated "PASS" or "FAIL”, but the outcome can still be of security concern and result in an overall “FAIL” for the device. An alternative result for a device is "ADVISORY", this means some security concerns exist with the device and it will require client referral for a decision on “PASS” or “FAIL”.
* Only required if this feature is supported/used on the device.
Test # | Test Description | Essential Pass | Pass, Fail, Info, N/A | Notes | Script?
1 | Confirm that the device can receive an IPv4 address from the DHCP (RFC 2131) server. | INFO | INFO | Yes. | Yes
2 | Confirm that the device can have a static IPv4 address set. | INFO | INFO | Yes. | No
3 | Device connects to switch and auto-negotiates (required) the highest speed possible - 10/100/1000 Mbit. | YES | PASS | Highest auto-negotiation to 100Mbit | Yes
4 | Confirm the current duplex value (e.g. full/half). | INFO | INFO | Full duplex supported. | Yes
5 | Ping the device and confirm there is a response (checking network connectivity and/or possible ICMP protocol block). | YES | PASS |  | Yes
6 | DHCP - accepts changes from the server - IP Address, DNS Servers. The client device should reacquire or verify its network parameters after port disconnect/toggle. | YES | PASS | After port toggle the controller accepts changes when the current lease time expires. | Yes
7 | Network disconnect/re-connect - device should resume connection seamlessly when interrupted. | YES | PASS | Device operated as normal. | Yes
8 | Note the MAC Address and the registered manufacturer from the IEEE Standards Association. | YES | PASS | 38:D1:35:04:06:12 Vendor / Company: Easyio Corporation Sdn. Bhd. | Yes
9 | Confirm if the device supports IPv6 - SLAAC (RFC 4862). | INFO | INFO | Yes, it supports IPv6. | Yes
10 | Confirm that the IPv6 address can be pinged/nmap scanned.* | INFO | INFO | Yes, device's IPv6 address can be pinged. | Yes
11 | Does the device have a secondary network port, if yes can it be disabled. | YES | FAIL | It has a secondary network port, it cannot be disabled through the web GUI/software. | No
12 | Are there any other means of creating a network connection to the device, (e.g. USB port for a network adapter). | INFO | INFO | No. | No
13 | Set the NTP server on a device and confirm that the time has synced correctly, required version is NTPv4 (RFC 5905). NTS support recommended. | YES | PASS | Note - The controller's NTP service was disabled as default. After enabling it, the NTP server was set to time.google.com where it was able to synchronise to the correct time. NTP version 4 is being used. | Yes
14 | Recording the data flow types from Wireshark traffic and note anything of concern or question. | INFO | INFO | ARP, DNS, ICMP, ICMPv6 (if IPv6 is enabled), TLSv1.2. Nothing unusual. | No
15 | Confirm the device supports DNS and receives DNS servers from DHCP and can set as static. | NO | INFO | Supports DNS and a static DNS can be set. | No
16 | Does the device use a webpage for device configuration. | INFO | INFO | Yes. | No
17 | *Web access TLS version - Minimum TLS 1.2 (RFC 5246), preferred TLS 1.3 (RFC 8446) (deprecated versions are required to be disabled). If both TLS 1.2 and 1.3 are enabled, then preference is have 1.2 disabled. | YES | PASS | Info - TLS 1.2 and 1.3 both enabled, no way to disable 1.2. | Yes
18 | *HTTPS used for web access with HTTP is a requirement to be disabled. | YES | PASS | HTTPS is enabled, and HTTP is disabled. | Yes
19 | *Device allows for replacement of self-signed certificate with an x509v3 certificate. | INFO | INFO | Yes. | No
20 | *What is the web server password policy (character limit, requirements, special characters). | INFO | INFO | A minimum of 12 characters, must include: - one lowercase character, - one uppercase character, - special character Note - cannot reset back to default password. "admin" credentials are now Password1234! | Yes
21 | *What cipher suites are supported by the server. Note if any are required to be disabled as part of the Nessus/Mozilla recommendations. | INFO | INFO | The following ciphersuites are old/weak and should be disabled: Accepted TLSv1.2 256 bits ECDHE-RSA-AES256-SHA384 Acceptable Ciphersuites: Preferred TLSv1.3 256 bits TLS_CHACHA20_POLY1305_SHA256 Accepted TLSv1.3 256 bits TLS_AES_256_GCM_SHA384 Accepted TLSv1.3 128 bits TLS_AES_128_GCM_SHA256 Preferred TLSv1.2 256 bits ECDHE-RSA-AES256-GCM-SHA384 | Yes
22 | What OS or other versioning information can be derived from the device. | INFO | INFO | From Nessus: OS: Unix (unable to find what version). From web GUI: Firmware Version : V1.0b20 Build Date : 2021-09-07 01:48:00 MCU Firmware Version : v1.1.3 | Yes
23 | Is any of the versioning information of security concern (e.g. outdated, end of support). | YES | PASS |  | No
24 | Check for Wi-Fi support. | INFO | INFO | Yes, Wi-Fi is supported; however, Wi-Fi is not to be used on the project for this device. | No
25 | *Confirm ability to disable/turn off Wi-Fi. | YES | N/A |  | No
26 | *If Wi-Fi is required, then WPA3-PSK should be supported. (Any mixed mode to support older encryption should not be used). | YES | N/A |  | No
27 | *If the device broadcasts an SSID then confirm the ability to change this. | YES | N/A |  | No
28 | What are the default credentials for all device services that are accessible and required for configuration. | INFO | INFO | Default admin credentials for the web GUI: username: admin password: hellocpt SSH: username sdcard password: 123456 | No
29 | Can the default credentials, including the username and password (password required), be changed. | YES | PASS | Only the password can be changed. | No
30 | Does the device have brute force protection for its credential based services and is this configurable. | NO | INFO | There is a brute force protection - after x amount of attempts there will be a timer before you can gain access to the controller gain. This cannot be configured. | Yes
31 | Does the device have multiple user accounts with different levels of privilege. If not required, can these be de-activated. | INFO | INFO | There are 5 user account types: Engineer, Manager, Operator, Viewer and admin. They can all have their access restricted through the admin user; however, even with the lowest level of access, they can still log into the controller and reboot/restart/save the controller from the webpage. It does not seem like these can be deactivated fully. | No
32 | Does the device require the use of SSH (RFC 4253). | INFO | INFO | No, but SSH is enabled. | Yes
33 | *If SSH is required to be used then review the connection log to ensure that SSH protocol version 2 is used. | YES | PASS | SSH version 2 is being used. | Yes
34 | *Test the ability to use public/private key authentication over using password authentication on the device SSH server. | INFO | N/A | SSH not required. | No
35 | What ports are shown as open from an Nmap/Nessus scan. | INFO | INFO | SSH on TCP Port 22 DNS TCP Port 53 SMB TCP Port 139 HTTPS TCP Port 443 CIFS TCP Port 445 | Yes
36 | Are any of the ports/services on those ports outside of the allowed whitelist under "Protocol Whitelist". | YES | FAIL | SMB TCP Port 139 CIFS TCP Port 445 | Yes
37 | What is the process of updating the firmware on the device. | INFO | INFO | Through the web GUI. | No
38 | Is the process of updating/patching the device deemed a security concern, e.g. physical access to device required, no OTA updates. | YES | PASS |  | No
39 | Does the device support BACnet/IP. | INFO | INFO | Yes. | No
40 | *Does the device support BACnet/SC (Secure Connect). | INFO | INFO | No. | No
41 | *What BACnet versioning information can be discovered from the device (YABE, nmap, PICS). | YES | PASS | From CPT tool BACnet network block: Firmware revision: 0.8.4 Protocol version: 1.14 Application version: 1.56 | Yes
42 | Does the device support 802.1x (RFC 3580) authentication. | INFO | INFO | Yes. | Yes
43 | *What types of 802.1x authentication are supported (EAP-TLS preferred). | INFO | INFO | MD5, TLS, Tunneled TLS, Protected EAP(PEAP) | No
44 | Nessus Scan - are there any identified risks that should be rectified. | YES | FAIL | See "01 Test - Nessus" tab for more info. | No
45 | Note any hardware specification/versioning information about the device. | INFO | INFO | Main Processor: MIPS 580 MHz Processor: ARM Cortex 48 MHz Flash Memory: 32MB RAM: 128MB | No
46 | 7-day network connectivity soak test. | YES | PASS |  | No

## 01 Test - Nessus
Results - Network Scan
Analysis and Concerns (If Any)
IP Forwarding (50686) - IP forwarding is enabled, this can be exploited by attackers to route packets through the host and potentially bypass network equipment (such as firewalls).
SSH (153953) - There is a weak key exchange algorithm enabled on the device (diffie-hellman-group1-sha1), it is recommended that this algorithm is disabled.
SMB (57608/96982/100871) - Signing is not required on the remote SMB server. Leading the SMB server more prone to man-in-the-middle attacks by an unauthenticated remote attacker. SMB version 1 enabled on port 445/TCP/CIFS - Microsoft has recommended to not use SMBv1 as it has a lack of security features.
HTTP Cookies (69826/85602) - When a cookie is not marked 'secure', the browser may send them back over an unencrypted link under certain circumstances. This could mean a remote attacker could intercept these cookie. The cookies should be inspected and the secure flag set to '1'. The cookie flagged up as unsecure is "CPTSESSID".
CSP (50344) - The missing security headers should be configured into the web server config file for Content-Secure-Policy frame-ancestors. Web server hardening is required.
SYN Scan (11219) - SSH TCP Port 22, TCP Port 53, SMB TCP Port 139, CIFS TCP Port 445 all open.