## TEST SYNOPSIS
General Test Information
Test Attempt | 1
Date Test Started - Date Test Finished | 08/05/2025 - 22/05/2025
System | Security
System Owner
Manufacturer | Pelco
Model | SMLE1-15V5-3H
Firmware Version | 5.14.0.38
Serial Number | 382412243832
Name Of Tester | Dhilen Patel
TEST RESULT | ADVISORY
Test Synopsis
Update 08/08/2025: Pelco have confirmed that the RTSP/video stream can be tunnelled over HTTPS. Therefore, the video stream is encrypted - this mitigates against the issue of RTSP being unencrypted, and therefore the test result has been changed from a fail to an advisory, and the below is no longer applicable. The advisory comes with the recommendation that the security contractor should ensure that RTSP/the video stream is tunnelled over HTTPS. Main failure point is RTSP being enabled. RTSP is unencrypted and should be disabled. There is currently no way to disable RTSP in the web interface and the manufacturer has not committed to employing secure RTSP in the future. To see the video stream via the RTSP URL, a username and password would need to be entered; however, due to it being unencrypted, the username is transmitted via plain text, which is not acceptable. Mitigations could include only allowing certain known-IP addresses to access the RTSP URL and employing complex passwords on the device. The RTSP port being used by the camera can be changed from the non-standard RTSP port in the web interface, to mitigate against an attacker from scanning the standard RTSP port numbers (T13 & T14). Other minor notes below. The minimum TLS version should be set to v1.3 in the network settings, as some cipher suites used in v1.2 are deemed weak (these are listed in T16.1). HTTP should be disabled - which can be done via the web browser - as it is unencrypted (T14). The HTTP headers do not include Content-Security-Policy (CSP) and X-Content-Type-Options. Consider adding to enhance the security of the device - implementing CSP will protect against Cross-Site Scripting (XSS) and data injection attacks, and X-Content-Type-Options being set would mitigate against MIME sniffing. It is also advised to add a refferrer policy, remove information around the server and replace the HTTP Digest Authentication with a more up-to-date authentication method. Brute force protection is implemented (T29); however, after 10 unsuccessful attempts, the user will be locked out for around 3-5 minutes regardless of whether they input the correct credentials or not. After the lockout time period, the user can log in with no problems. This is good protection for when the camera is attempted to be brute forced from multiple points, but note that it could cause an engineer to be locked out during the lockout period (denial of service). This should not be a major issue as the cameras can also be controlled via their command center, however... This issue can be mitigated by only allowing certain, known, IP addresses to be able to access the camera's webpage.

## TESTPLAN
Test Results Explained PASS - The device passed the specific test with no issues. FAIL - The device failed the specific test. Where the reasons for the failure will be specified in the test comments. ADVISORY - The test is close to passing, but further configuration is required to get the device to be compliant. I.e. HTTP is by default open, which is unencrypted, but you are able to disable HTTP in the device's web interface. N/A - The test is not applicable to the device and therefore was not conducted.
Test Number | Brief Description | Test Description | Essential Pass | Test Result | Test Comments | Script?
1 | Initial Switch Connection | When device is plugged in to a switch, it auto-negotiates a speed and supports full duplex. | YES | PASS | Full duplex supported, auto-negotiates to 1000Mbit/s. You can manually set the speed and duplex in the device's web interface in the "Network & Security" section. | Yes
2 | DHCP #1 | Device accepts address and related data by DHCP. | YES | PASS |  | Yes
3 | DHCP #2 | Device accepts changed address from the server without the need of a reboot or port toggle. | YES | PASS | DHCP address obtained on a new range. | Yes
4 | Ping | Device responds to ping requests. | YES | PASS |  | Yes
5 | MAC Address | Device MAC address is registered to a manufacturer. | YES | PASS | MAC:00:04:7D:D7:D1:58 Vendor: Motorola Solutions Inc. Company Address: 500 W Monroe Street, Ste 4400 Chicago IL US 60661-3781 Last Update: 28/01/2021 | Yes
6 | IPv6 #1 | Device supports IPv6 addressing. | NO | PASS |  | Yes
7 | IPv6 #2 | Device supports SLAAC/DHCP for IPv6 addressing. | NO | PASS | Accepts DHCPv6 and static IPv6 addressing. | Yes
8 | Network Disconnection | The device continues to operate locally during a network disconnection. | YES | N/A | Device is PoE, so without the ethernet connection, it would be powered off. | No
9 | Network Reconnection | Device automatically re-discovers network connection when network cable is plugged back in. | YES | PASS | Network cable toggled, device is able to re-establish a network connection. | Yes
10 | NTP | Device can automatically synchronise to NTP highest version supported (ideally version 4) | YES | PASS | NTP version 4 traffic seen. | Yes
11 | Data Flow | Record the devices data flow types. endpoints and keepalive traffic. There should be no unencrypted communications. | YES | PASS | No unusual traffic recorded. | No
12 | DNS | Device supports DNS and static DNS server addressing. | YES | PASS | Both static and automatic DNS addressing supported. | No
13 | Open Ports | List the network ports that are currently open on the device. | YES | FAIL | Port 80: HTTP Port 322: RTSPS Port 443: HTTPS Port 554: RTSP Port 555: RTSP (Replay Port) Port 9090: WebRTC Port | Yes
14 | Discouraged Ports | List the network ports that are currently open, but should be closed (i.e. due to being unencrypted). | YES | FAIL | Port 554 and 555: RTSP is unencrypted and should be disabled. Disabling RTSP cannot be done through the web GUI. Port 80: HTTP should be disabled. This can easily be done via the web GUI, in "Network and Security" the checkbox "Enable HTTP connections" can be unticked. | Yes
15 | TLS Version | Where the device utilises TLS, list the lowest version of TLS supported. This should be TLSv1.2 or above. | YES | PASS | The minimum TLS version can be specified in the web interface - the minimum is TLS v1.2 as default. The minimum TLS can also be set to v1.3. | Yes
16.1 | Ciphersuites | List the ciphersuites supported by the device and highlight any that are deemed as weak by Mozilla standards. | NO | PASS | The different encryption engines and their associated ciphers are listed (the highlighted ciphers are deamed weak), this is when TLSv1.2 is set in the web GUI: OpenSSL: TLS_AES_128_GCM_SHA256 TLS_AES_256_GCM_SHA384 TLS_CHACHA20_POLY1305_SHA256 ECDHE-RSA-AES128-GCM-SHA256 ECDHE-RSA-AES256-GCM-SHA384 ECDHE-RSA-CHACHA20-POLY1305 DHE-RSA-AES128-GCM-SHA256 DHE-RSA-AES256-GCM-SHA384 DHE-RSA-AES128-SHA256, DHE-RSA-AES256-SHA256, AES128-SHA256, AES256-SHA256 FIPS 140-2: TLS_AES_128_GCM_SHA256 TLS_AES_256_GCM_SHA384 ECDHE-RSA-AES128-GCM-SHA256 AES128-SHA256, AES256-SHA256 NXP TPM: TLS_AES_128_GCM_SHA256 TLS_AES_256_GCM_SHA384 ECDHE-ECDSA-AES128-GCM-SHA256 ECDHE-ECDSA-AES256-GCM-SHA384 ECDHE-ECDSA-AES128-SHA256, ECDHE-ECDSA-AES256-SHA384 Refer to below on why this is a pass, despite weak ciphers. | Yes
16.2 | Ciphersuites Continued… | List the ciphersuites supported by the device and highlight any that are deemed as weak by Mozilla standards. | YES | PASS | The different encryption engines and their associated ciphers are listed when the minimum TLS version is set to v1.3: TLS_AES_128_GCM_SHA256 TLS_AES_256_GCM_SHA384 TLS_CHACHA20_POLY1305_SHA256 The above cipher suites are deemed recommended and secure. This means the issue of the weak ciphers can be resolved by setting the camera to a minimum TLS version of 1.3. | Yes
17 | Unencrypted Web Access | The device does not accept unencrypted web traffic and supports x509 certificates. | YES | PASS | HTTP can be disabled, therefore, HTTPS/port 443 can be used for secure webpage access. New x509 certificates can be uploaded to the device via the webpage in "Network and Security" and "Certificates". | Yes
18 | 802.1x | Device supports 802.1x and supports EAP-TLS. | NO | PASS | EAP-TLS supported. | Yes
19 | Credentials | Confirm that the default credentials on the device can be changed. | YES | PASS | New users can be added via the web interface under "Network and Security" and "Users". | No
20 | BACnet Version | Record the BACnet version and traffic to and from the device. | YES | N/A |  | Yes
21 | BACnet PIC/BIBB | Confirm the device has a valid BACnet PIC and BIBB statement. | YES | N/A |  | No
22 | Wi-Fi Supported | The device supports one or more of the following Wi-Fi standards: 802.11g / 802.11n / 802.11ac / 802.11ax | YES | N/A |  | No
23 | Wi-Fi Disablement | Wi-Fi can be disabled on the device. | YES | N/A |  | No
24 | Wi-Fi Encryption | Wi-Fi supports WPA2-AES as a minimum. | YES | N/A |  | No
25 | PoE | List the PoE standards supported by the device. | NO | PASS | 30 W IEEE 802.3at Type 2 (PoE+), or can be powered with 24 VDC ± 10 %; 24 VAC rms ± 10 %, 50 or 60 Hz | No
26 | SOAK | Leave the device connected to the network for seven days, check switch logs to ensure the port remained stable and the device can still be reached. | YES | PASS | Nothing unusual. | No
27 | ADDITIONAL INFO | Device is scanned for any further vulnerabilities, please refer to the "Additional Info" tab. | YES | PASS | No serious vulnerabilities identified. Note the below: Consider hiding information about the server and no Content-Security-Policy (CSP), referrer-policy, X-Content-Type-Options set in the HTTP header. HTTP Digest Auth could be replaced with a more up-to-date authentication, i.e. mutual TLS. | No
28 | Software/OS | Identify the software/OS version information about the device. | NO | N/A | No software information could be derived. | No
29 | Brute Force | Device employs brute force protection on all of it's credential-based services. | YES | PASS | After 10 unsuccessful attempts logging into the webpage, a "loginLockout" message will appear. The user will then not be able to log in for a certain period of time (around 3-5 minutes) regardless of if they input the correct credentials or not. | Yes
30 | Session Expiry | Device logs out the user on inactivity after a certain period of time. | NO | PASS | Webpage logged out after a period of inactivity. | Yes
31 | Firmware Upgrades | Confirm how the firmware of device can be upgraded. | NO | PASS | Firmware upgrades can be done via the webpage or the command center. | No

## ADDITIONAL INFO
Additional Device Information
Medium - SSL/TLS: Server certificate comes default as an unsigned Pelco manufacturer certificate (and cannot be trusted, due to being self-signed). The certificate can be replaced via the web GUI, so this is not an issue. Low: Missing security header - Content-Security-Policy (CSP). CSP is used to prevent a variety of attacks, such as Cross-Site Scripting (XSS). It is recommended to set this header, as there are multiple variations available; select the one that provides the best protection for the resources on your webpages. Low: Missing security header - X-Content-Type-Options. Used to prevent MIME sniffing, recommendation is to set the header, i.e. X-Content-Type: nosniff. Low: Missing security header - Referrer-Policy. If the device sends the user to another website/service, the refer (i.e. the device's IP) will be seen. Setting the reffer-Policy header would shield the referer's information. This is not a major issue, as the camera does not have links to external services via it's webpage.