## TEST SUMMARY
General Test Information
Test Attempt
Date Test Started - Date Test Finished
System
System Owner
Manufacturer
Model
Firmware Version
Serial Number
Name Of Tester
TEST RESULT
Test Summary

## TESTPLAN
Test Results Explained PASS - The device passed the specific test with no issues. FAIL - The device failed the specific test. Where the reasons for the failure will be specified in the test comments. ADVISORY - The test is close to passing, but further configuration is required to get the device to be compliant. E.g. HTTP is open by default, which is unencrypted, but you are able to disable HTTP in the device's web interface. INFO - The test is for information only and may not cause the device to pass/fail. Note that depending on the test result, an INFO only test result can cause the device to fail. N/A - The test is not applicable to the device and therefore was not conducted.
Test Number | Brief Description | Test Description | Script? (Yes/No) | Essential Pass | Test Result | Test Comments
1 | Initial Switch Connection | When device is plugged in to a switch, it auto-negotiates a speed and supports full duplex. | Yes | YES
2 | Static IP | Confirm that the device can have a static IPv4 address set. | No | YES
3 | DHCP #1 | EDQ runs a DHCP server on the tester host; the device accepts an IP address, subnet, gateway if configured, DNS server, and NTP server address from EDQ DHCP. | Yes | YES
4 | DHCP #2 | After the EDQ DHCP offer range changes, the device accepts an address from the new range without needing a reboot or port toggle. | Yes | YES
5 | DNS Support | Device supports DNS and static/dynamic DNS addressing. | Yes (only the dynamic DNS part) | YES
6 | Hostname Resolutions | Can M2M connections be made via hostname rather than IP, e.g. MQTT Broker connection? | No | YES (IoT GATEWAYS ONLY)
7 | Ping | Device responds to ping requests. | Yes | YES
8 | MAC Address | Note the MAC address and confirm it is registered to a manufacturer. | Yes | YES
9 | IPv6 #1 | Device supports IPv6 addressing. | Yes | INFO
10 | IPv6 #2 | Device supports SLAAC/DHCP for IPv6 addressing. | Yes | INFO
11 | Network Reconnection | Device automatically re-discovers network connection when network cable is toggled. | Yes | YES
12 | NTP | Device can automatically synchronise to NTP highest version supported (ideally version 4) | Yes | YES (IoT GATEWAYS ONLY)
13 | Data Flow | Record the devices data flow types. endpoints and keepalive traffic. There should be no unencrypted communications. | No | YES
14 | Secondary Device Access | Check the device for secondary ports and/or any other means of creating a network connection to the device. | No | INFO
15 | Open Ports | List the network ports that are currently open on the device. | Yes | INFO
16 | Discouraged Ports | List the network ports that are currently open, but should be closed (e.g. due to being unencrypted or unused). | Yes (semi-automated) | YES
17 | TLS Version | Where the device utilises TLS, list the lowest version of TLS supported. This should be TLSv1.2 or above. | Yes | YES
18 | Ciphersuites | List the ciphersuites supported by the device and highlight any that are deemed as weak by Mozilla standards. | Yes (list the ciphers, don't have to say if weak/strong etc) | INFO
19 | Unencrypted Web Access | The device does not accept unencrypted web traffic and supports x509 certificates. | No | YES
20 | x509 Certificate Updates | Device allows for replacement of self-signed certificate with an x509 certificate. | No | INFO
21 | 802.1x | Device supports 802.1x and supports EAP-TLS. | Yes | INFO
22 | BACnet/IP Support and BACnet/IP Version | Does the device support BACnet/IP? Record the BACnet version and traffic to and from the device. | Yes (semi-automated) | INFO
23 | BACnet PIC/BIBB | Confirm the device has a valid BACnet PIC and BIBB statement. | No | INFO
24 | SSH | Does the device require the use of SSH? If required, confirm SSH protocol version 2 is being used. | Yes | YES
25 | MQTT Support | Does the device support MQTT? If so state the MQTT version supported If not, state how the device can send data to a broker (e.g. via HTTPS or via middleware). | No | YES (IoT GATEWAYS ONLY)
26 | MQTT Custom Payloads | Does the device support UDMI JSON payload creation? Does the device allow custom JSON payloads to be created? | No | YES (IoT GATEWAYS ONLY)
27 | MQTT Write-back | Does the device allow commands to be sent via MQTT? | No | YES (IoT GATEWAYS ONLY)
28 | MQTT Over TLS | Does the device support MQTT over TLS? | No | YES (IoT GATEWAYS ONLY)
29 | MQTT Authentication #1 | Is Client Certificate authentication for MQTT supported using X.509 certificates? | No | YES (IoT GATEWAYS ONLY)
30 | MQTT Authentication #2 | Is Username/Password authentication for MQTT supported? | No | YES (IoT GATEWAYS ONLY)
31 | PKI Integration | Can custom CA certificates be installed into the devices trust store to enable integration into a private PKI? | No | YES (IoT GATEWAYS ONLY)
32 | Wi-Fi Standards Supported | The device supports one or more of the following Wi-Fi standards: 802.11g / 802.11n / 802.11ac / 802.11ax | No | YES
33 | Wi-Fi Disablement | If not required for normal operations: Wi-Fi can be disabled on the device. | No | YES
34 | Wi-Fi Encryption | Wi-Fi supports WPA2-AES as a minimum. | No | YES
35 | PoE | List the PoE standards supported by the device. | No | INFO
36 | Credentials | Confirm the default credentials on the device and confirm the credentials can be changed for each credential-based service. | No | YES
37 | Login Credentials Policy | Confirm the login credentials policy on all services that require username/password authentication. | No | INFO
38 | Brute Force | Device employs brute force protection on all of it's credential-based services. | Yes | YES
39 | Session Expiry | Device logs out the user on inactivity after a certain period of time. | Yes | INFO
40 | Firmware Upgrades | Confirm how the firmware of device can be upgraded. | No | INFO
41 | Software/OS Info | List any software/OS version information obtained from the device. | No | INFO
42 | Additional Information | Device is scanned for any further vulnerabilities, please refer to the "Additional Info" tab. | No | YES
43 | SOAK | Leave the device connected to the network for seven days, check switch logs to ensure the port remained stable and the device can still be reached. | No | YES

## ADDITIONAL INFORMATION
Additional Device Information 1
Additional Device Information 2